## Sheet1
Potencia DC [kWp] | Potencia AC [kWn] | Producción específica P50 [kWh/kWp/año] | Generación neta esperada P50 [MWh/año] | Performance Ratio (PR) [%] | Módulos Fotovoltaicos | Inversores | Base de datos meteorológicos | Capacidad del Transformador [kW]
1376 | 990 | 1625 | 2234.6 | 83.88 | LONGi solar LR8-66HYD-655M (655 Wp) - 2100 unidades | Huawei Technologies SUN2000-330KTL-H1 - 3 unidades | Cluster_GuayacÃ¡n_y_el_tigre SolarGIS - TMY System summary Grid-Connected System Tables on a building Simulation for year no 1 Orientation #1 Near Shadings User's needs Fixed plane Linear shadings : Fast (table) Unlimited load (grid) Tilt/Azimuth 10 / 0° System information PV Array Inverters Nb. of modules 2100units Nb. of units 3units Pnom total 1376kWp Total power 900kVA Grid power limit 990kWac Grid lim. Pnom ratio 1.389 Results summary Produced Energy 2234.6MWh/year Specific production 1625kWh/kWp/year Perf. Ratio PR 83.88% Apparent energy 2234.6MVAh/year Bifacial perf. ratio 81.67% Table of contents Project and results summary 2 General parameters, PV Array Characteristics, System losses 3 Near shading definition - Iso-shadings diagram 6 Main results 7 Loss diagram 8 Predef. graphs 9 P50 - P90 evaluation 10 Single-line diagram 11 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 2/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 General parameters Grid-Connected System Tables on a building Orientation #1 Fixed plane Sheds configuration Sizes Tilt/Azimuth 10 / 0° Nb. of sheds 25units Sheds spacing 9.38m Set of tables Sensitive width 7.19m Shading limit angle GCR Shading 76.6% Limit profile angle 28.6° Models used Horizon Near Shadings Transposition Perez Free Horizon Linear shadings : Fast (table) Diffuse Imported Circumsolar separate Bifacial system definition User's needs Orientation #1 Unlimited load (grid) Bifacial system Model Unlimited Sheds 2D Model Bifacial model geometry Sheds spacing 9.38m Sheds width 7.19m Limit profile angle 28.6° GCR Bifacial 76.6% Height above ground 1.50m Nb. of sheds 15units Bifacial model definitions Ground albedo 0.20 Bifaciality factor 75% Rear shading factor 5.0% Rear mismatch loss 10.0% Shed transparent fraction 0.0% Grid injection point Grid power limitation Power factor Active power 990kWac Cos(phi) (lagging) 1.000 Pnom ratio 1.389 Limit applied at the inverter level PV Array Characteristics PV module Inverter Manufacturer LONGi solar Manufacturer Huawei Technologies Model LR8-66HYD-655M Model SUN2000-330KTL-H1 (Custom parameters definition) (Custom parameters definition) LONGi_LR8-66HYD-655M.PAN Unit Nom. Power 300kVA Unit Nom. Power 655Wp Number of inverters 3units Number of PV modules 2100units Total power 900kVA Nominal (STC) 1376kWp Operating voltage 550-1500V Modules 75 string x 28In series Max. power (=>30°C) 330kVA At operating cond. (50°C) Pnom ratio (DC:AC) 1.53 Pmpp 1286kWp Leading limit Cos(phi) min 0.800 U mpp 1079V Lagging limit Cos(phi) min 0.800 I mpp 1192A Power sharing within this inverter 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 3/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 PV Array Characteristics Total PV power Total inverter power Nominal (STC) 1376kWp Total power 900kVA Total 2100modules Max. power 990kWac Module area 5672m² Number of inverters 3units Cell area 5297m² Pnom ratio 1.53 Array losses Array Soiling Losses Thermal Loss factor DC wiring losses Loss Fraction 3.0% Module temperature according to irradiance Global array res. 4.2mΩ Uc (const) 29.0W/m²K Loss Fraction 0.43% at STC Uv (wind) 0.0W/m²K/m/s LID - Light Induced Degradation Module Quality Loss Module mismatch losses Loss Fraction 1.0% Loss Fraction -0.70% Loss Fraction 2.00% at MPP Strings Mismatch loss Module average degradation Loss Fraction 0.15% Year no 1 Loss factor 0.35%/year Imp / Vmp contributions 50% / 50% Mismatch due to degradation Imp RMS dispersion 0.4%/year Vmp RMS dispersion 0.4%/year IAM loss factor Incidence effect (IAM): User defined profile 0° 50° 60° 65° 70° 75° 80° 85° 90° 1.000 1.000 1.000 0.990 0.959 0.910 0.841 0.680 0.000 System losses Unavailability of the system Auxiliary losses Time fraction 1.4% Proportional to Power 4.0W/kW 5.0days, 0.0 kW from Power thresh. 3periods AC wiring losses Inv. output line up to MV transfo Inverter voltage 800Vac tri Loss Fraction 0.73% at STC Inverter: SUN2000-330KTL-H1 Wire section (3 Inv.) Alu 3 x 3 x 240 mm² Average wires length 78m MV line up to Injection MV Voltage 33kV Wires Alu 3 x 50 mm² Length 36m Loss Fraction 0.00% at STC 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 4/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 AC losses in transformers MV transfo Medium voltage 33kV Transformer from Datasheets Nominal power 1250kVA Iron Loss (24/24 Connexion) 1.25kVA Iron loss fraction 0.10% of PNom Copper loss 12.50kVA Copper loss fraction 1.00% at PNom Coils equivalent resistance 3 x 5.12mΩ 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 5/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 Near shadings parameter Perspective of the PV-field and surrounding shading scene Iso-shadings diagram Orientation #1 - Fixed plane, Tilts/azimuths: 10°/ 0° 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 6/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 Main results System Production Produced Energy (P50) 2234.6MWh/yearSpecific production (P50) 1625kWh/kWp/year Perf. Ratio PR 83.88% Produced Energy (P90) 2134.3MWh/yearSpecific production (P90) 1552kWh/kWp/year Bifacial perf. ratio 81.67% Produced Energy (P95) 2106.1MWh/yearSpecific production (P95) 1531kWh/kWp/year Apparent energy 2234.6MVAh/year Normalized productions (per installed kWp) Performance Ratio PR Balances and main results GlobHor DiffHor T_Amb GlobInc GlobEff EArray E_Grid PR kWh/m² kWh/m² °C kWh/m² kWh/m² MWh MWh ratio January 173.9 79.80 18.80 186.4 177.6 220.2 198.3 0.774 February 154.1 76.05 18.39 160.3 152.8 189.9 183.8 0.833 March 168.3 91.37 18.68 169.9 161.8 202.3 195.8 0.838 April 158.4 85.10 18.29 154.7 147.1 187.8 181.8 0.854 May 152.9 77.66 18.58 145.1 137.6 180.5 174.6 0.875 June 154.1 77.99 19.38 144.2 136.8 182.0 176.3 0.889 July 163.8 76.15 18.22 153.7 146.1 193.4 187.3 0.886 August 170.7 78.59 18.50 164.4 156.6 200.6 194.2 0.859 September 161.9 78.84 18.32 161.4 153.7 194.7 180.8 0.814 October 160.5 79.47 17.58 165.2 157.4 196.9 190.6 0.839 November 152.6 74.29 17.83 161.9 154.0 192.7 186.4 0.837 December 157.6 75.16 18.51 169.7 161.4 202.0 184.9 0.792 Year 1929.0 950.48 18.42 1936.9 1843.1 2343.0 2234.6 0.839 Legends GlobHor Global horizontal irradiation EArray Effective energy at the output of the array DiffHor Horizontal diffuse irradiation E_Grid Energy injected into grid T_Amb Ambient Temperature PR Performance Ratio GlobInc Global incident in coll. plane GlobEff Effective Global, corr. for IAM and shadings 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 7/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 Loss diagram 1929 kWh/m² Global horizontal irradiation +0.4% Global incident in coll. plane -1.3% Near Shadings: irradiance loss -3.0% Soiling loss factor -0.6% IAM factor on global +0.0% Ground reflection on front side Bifacial Global incident on ground 463 kWh/m² on 7402 m² -80.0% (0.20 Gnd. albedo) Ground reflection loss -43.8% View Factor for rear side +2.4% Sky diffuse on the rear side +0.0% Beam effective on the rear side -5.0% Shadings loss on rear side ( 1843 + 0.75 * 66.1 ) kWh/m² 3.6%Global Irradiance on rear side (66 kWh/m²) * 5672 m² coll. Effective irradiation on collectors efficiency at STC = 24.27% PV conversion, Bifaciality factor = 0.75 2605.6 MWh Array nominal energy (at STC effic.) -0.2% Module Degradation Loss ( for year #1) -0.1% PV loss due to irradiance level -2.9% PV loss due to temperature +0.7% Module quality loss -1.0% LID - Light induced degradation -2.1% Mismatch loss, modules and strings -0.3% Mismatch for back irradiance -0.3% Ohmic wiring loss 2451.1 MWh Array virtual energy at MPP -1.3% Inverter Loss during operation (efficiency) -4.5% Inverter Loss over nominal inv. power 0.0% Inverter Loss due to max. input current 0.0% Inverter Loss over nominal inv. voltage 0.0% Inverter Loss due to power threshold 0.0% Inverter Loss due to voltage threshold 2311.3 MWh Available Energy at Inverter Output -0.4% Auxiliaries (fans, other) -0.4% AC ohmic loss -1.1% Medium voltage transfo loss 0.0% MV line ohmic loss -1.5% System unavailability 2234.6 MWh Active Energy injected into grid 0.0 MVARh Reactive energy to the grid, Yearly effective cos(Phi) = 1.000 2234.6 MVAh Apparent energy to the grid 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 8/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 Predef. graphs Daily Input/Output diagram System Output Power Distribution 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 9/11 Project: Clúster Guayacán y el Tigre Variant: Clúster 2 - Proyecto Solar Sabina PVsyst V8.0.18 SUNCOLOMBIA SAS (Colombia) VCF, Simulation date: 26/11/25 08:24 with V8.0.18 P50 - P90 evaluation Weather data Simulation and parameters uncertainties Source SolarGIS PV module modelling/parameters 1.0% Kind TMY, multi-year Inverter efficiency uncertainty 0.5% Year-to-year variability(Variance) 3.0% Soiling and mismatch uncertainties 1.0% Specified Deviation Degradation uncertainty 1.0% Climate change 0.0% Global variability (weather data + system) Annual production probability Variability (Quadratic sum) 3.5% Variability 78MWh P50 2235MWh P90 2134MWh P95 2106MWh Probability distribution 26/11/25 PVsyst Licensed to SUNCOLOMBIA SAS (Colombia) Page 10/11 PVsyst V8.0.18 VCF, Simulation date: 26/11/25 08:24 with V8.0.18 | 1250